## UFLS
UNDER-FREQUENCY LOAD SHEDDING (UFLS) REVISION 2024
Stage Label | Grid | Substation | Substation_id | voltage | Assigned Feeders | CB | Freq1 | Delay1 (s) | Freq2 | Delay2 (s)
Stage: Ride Through | Kuantan | Gebeng Industri | GBID | 132 | KSTL 1 & 2 | 105 & 405 | 49.3 | 0 | n/a | n/a
| Johor Bahru | Tanjung Langsat | TLST | 132 | TLTP (Titan Petrochemicals) | 505 | 49.3 | 0 | n/a | n/a
| Johor Bahru | Pasir Gudang Darat | PGDT | 132 | TTAN 1 & 2 | 905 & 1005 | 49.3 | 0 | n/a | n/a
| Johor Bahru | Pasir Gudang Ind Est | PGIE | 132 | ASTM 1 & 2 | 805 & 905 | 49.3 | 0 | n/a | n/a
| Johor Bahru | Tanjung Langsat Industrial Estate | TLIE | 275 | BSTL 1 & 2 | L15 & L25 | 49.3 | 0 | n/a | n/a
| Kuantan | Tanjung Gelang | TGLN | 132 | JDSI 1 & 2 | 505 & 605 | 49.3 | 0 | n/a | n/a
| Dungun | Telok Kalong | TKLG | 275 | Perwaja 1 & 2 | L15 & L25 | 49.3 | 1 | n/a | n/a
| Selangor | Olak Lempit | OLPT | 275 | MGST 1 & 2 | L75 & L85 | 49.3 | 0 | n/a | n/a
| Selangor | Bukit Raja GIS | BRGS | 132 | ASMB 1 & 2 | 11130, 11230, 11330 | 49.3 | 0 | n/a | n/a
| Selangor | Bukit Raja GIS | BRGS | 132 | MSWK | 7130, 7230 | 49.3 | 0 | n/a | n/a
| Perda | Bukit Tengah | BTGH | 132 | SRON 2 | 905 | 49.3 | 0 | n/a | n/a
| Perda | Bedong | BDNG | 275 | PWGR 1 & 2 feeders | L35 & L45 | 49.3 | 0 | n/a | n/a
| Perda | Prai Industrial | PRID | 132 | SRON & SRNW | 505 & 605 | 49.3 | 0 | n/a | n/a
| Perda | SKS Prai | SKSP | 132 | MWTA 1 & 2 | 105 & 205 | 49.3 | 0 | n/a | n/a
Stage 1: 49.2Hz | Johor Bahru | Cahaya Baru | CBRU | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a
| Johor Bahru | Pasir Gudang Darat | PGDT | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a
| Johor Bahru | Tampoi Industries | TMPI | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a
| Perda | Sungai Ara (GIS) | SARA | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a
| Kuantan | Pekan Industri AIP | PKNI | 33 | 132/33kV T1 & T2 | 1T0 & 2T1 | 49.2 | 0 | n/a | n/a
| Ayer Keroh | Hicom Pegoh | HPGH | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a
| Seremban | Enstek | ESTK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a
| Seremban | Kg. Repah | KRPH | 11 | 132/11kV T1 & T2 | 30 & 32 | 49.2 | 0 | n/a | n/a
| Ipoh | Pengkalan Industri | PKID | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.2 | 0 | n/a | n/a
| Ipoh | Pengkalan Industri | PKID | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.2 | 0 | n/a | n/a
| Ipoh | Kinta Valley Resort | KVRT | 33 | 132/33kV T3 & T4 | 3T0, 4T0 & 1W0 | 49.2 | 0 | n/a | n/a
| Ipoh | Menglembu | MLBU | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.2 | 0 | n/a | n/a
| Selangor | Setia Alam | STIA | 33 | 132/33kV T1 & T2 | 1T0 & 2T1 | 49.2 | 0 | n/a | n/a
| Kuala Lumpur | Damansara City | DCTY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a
| Kuala Lumpur | Manjalara | MJLR | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a
| Kuala Lumpur | Sri Hartamas | SHMS | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a
| Kuala Lumpur | Suncity GIS | SCTY | 33 | 132/33kV T1 & T2 | 1T0 & 2T2 | 49.2 | 0 | n/a | n/a
| Kuala Lumpur | Cheras Jaya | CJYA | 33 | 132/33kV T1, T2 & T3 | 1T0 & 2T0 & 3T0 | 49.2 | 0 | n/a | n/a
| Kuala Lumpur | Danau Desa | DDSA | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.2 | 0 | n/a | n/a
| Alor Setar | Mergong | MGON | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.2 | 0 | n/a | n/a
| Alor Setar | Pauh | PAUH | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.2 | 0 | n/a | n/a
Stage 2: 49.1Hz | Ipoh | Temoh | TMOH | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49.1 | 0 | n/a | n/a
| Ipoh | Kelebang | KLBG | 33 | 132/33kV T3 & T4 | 3T0, 4T0 & 1W0 | 49.1 | 0 | n/a | n/a
| Ipoh | New Khantan | NKAN | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a
| Ipoh | Tasik | TASK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a
| Kuala Lumpur | SPPK Cheras | SPKC | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 1W0 & 5T0 | 49.1 | 0 | n/a | n/a
| Kuala Lumpur | National University | NUNI | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.1 | 0 | n/a | n/a
| Johor Bahru | Plentong | PLTG | 230 | WAV8 1 & 2 | H10 & H20 | 49.1 | 0 | n/a | n/a
| Johor Bahru | Tebrau | TBRU | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a
| Kuantan | Kampung Awah | KAWA | 132 | KRYG 1 & 2 | 305 & 405 | 49.1 | 0 | n/a | n/a
| Seremban | Tuanku Jaafar (GIS) | TJGS | 132 | SHEL 1 & 2 | 505 & 605 | 49.1 | 0 | n/a | n/a
| Selangor | Hicom | HCOM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a
| Selangor | Shah Alam East | SHAE | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 5T0 | 49.1 | 0 | n/a | n/a
| Selangor | Shah Alam South | SHAS | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a
| Kota Bharu | Panchor | PCOR | 33 | 132/33kV T2 & T3 & T4 | 2T0, 3T0 & 4T0 | 49.1 | 0 | n/a | n/a
| Kluang | Johor Tengah | JTGH | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.1 | 0 | n/a | n/a
| Perda | Seberang Jaya | SJAY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49.1 | 0 | n/a | n/a
| Perda | Taman Intan | INTN | 33 | 132/33kV T3 & T4 | 3T0&4T0 | 49.1 | 0 | n/a | n/a
| Perda | Taman Intan | INTN | 11 | 132/11kV T1 & T2 | 31&32 | 49.1 | 0 | n/a | n/a
| Ayer Keroh | Malacca Power Station | MPSS | 11 | 132/11kV T1 & T2 | 31 & 32 | 49.1 | 0 | n/a | n/a
Stage 3: 49.0Hz | Kota Bharu | Tunjung | TJUG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a
| Ayer Keroh | Malim Jaya | MJYA | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a
| Ayer Keroh | Muar | MUAR | 11 | 132/11kV T2 & T3 | 32 & 33 | 49 | 0 | n/a | n/a
| Selangor | Bukit Rajah | BRGS | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a
| Selangor | Port Klang P/S | PKLG | 132 | IGBK 1 & 2 | 705 & 805 | 49 | 0 | n/a | n/a
| Selangor | Bukit Beruntung | BBTG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a
| Kuantan | Bandar Indra Mahkota | BIMK | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a
| Kuantan | Bandar Indra Mahkota | BIMK | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a
| Kuantan | Bentong | BNTG | 11 | 132/11kV T1 & T2 | 31 & 32 | 49 | 0 | n/a | n/a
| Perda | Butterworth North | BWTN | 33 | 132/33 kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a
| Perda | Butterworth North | BWTN | 11 | 132/11kV T5 | 35 | 49 | 0 | n/a | n/a
| Perda | Prai GIS | PRGS | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a
| Kuala Lumpur | Serdang Raya | SRDR | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a
| Kuala Lumpur | Ampang GIS | AMPG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a
| Kuala Lumpur | Air Hitam | AHTM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a
| Kuala Lumpur | Bukit Jalil | BJLL | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 49 | 0 | n/a | n/a
| Kuala Lumpur | Balakong | BLKG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 49 | 0 | n/a | n/a
Stage 4: 48.9Hz | Kota Bharu | Kota Bharu | KBRU | 33 | 132/33kV T1 & T3 & T5 | 1T0 & 3T0 & 5T0 | 48.9 | 0 | n/a | n/a
| Selangor | PJ South | PJST | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a
| Johor Bahru | Pasir Gudang Town Centre | PGTC | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a
| Johor Bahru | Pasir Gudang Ind Est | PGIE | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a
| Johor Bahru | Pasir Gudang Ind Est | PGIE | 22 | 132/22kV T3 | 3T0 | 48.9 | 0 | n/a | n/a
| Selangor | Puchong Jaya | PCHJ | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a
| Selangor | New Subang Uda | NSDA | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a
| Kuala Lumpur | Sri Damansara | SDAM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a
| Kuala Lumpur | New SEA Park | NSPK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a
| Kuala Lumpur | Serdang New | SRDN | 33 | 132/33kV T1 & T2 | 1T0&2T0 | 48.9 | 0 | n/a | n/a
| Seremban | Sendayan | SDYN | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.9 | 0 | n/a | n/a
| Seremban | Lukut | LKUT | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.9 | 0 | n/a | n/a
| Kuantan | Tanjong Gelang | TGLN | 11 | 132/11kV T1 & T2 & T3 | 31 & 32 & 33 | 48.9 | 0 | n/a | n/a
Stage 5: 48.8Hz | Alor Setar | Kota Setar | KSTR | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.8 | 0 | n/a | n/a
| Kuala Lumpur | Kg Chempaka | KCPK | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a
| Selangor | New Rawang | NRWG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a
| Selangor | Bukit Kapar | BKPR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.8 | 0 | n/a | n/a
| Selangor | Temasya | TMSY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a
| Ayer Keroh | Kelemak | KLMK | 132 | MTNH 1 & 2 | 105 & 205 | 48.8 | 0 | n/a | n/a
| Seremban | Rantau | RTAU | 132 | TKMG 1 & 2 | 105 & 205 | 48.8 | 0 | n/a | n/a
| Seremban | Paroi | PROI | 132 | TJID 1 & 2 | 105 & 205 | 48.8 | 0 | n/a | n/a
| Seremban | Rasah | RASA | 132 | Satria & TTJF | 505 & 605 | 48.8 | 0 | n/a | n/a
| Kuantan | Bentong South | BNTS | 132 | BNTG & RBDR | 205 & 405 | 48.8 | 0 | n/a | n/a
| Kuantan | Kg. Awah | KAWA | 132 | JNKA & JTUT | 205 & 705 | 48.8 | 0 | n/a | n/a
| Perda | Air terjun | ATJN | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.8 | 0 | n/a | n/a
| Perda | Gurun | GRUN | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.8 | 0 | n/a | n/a
| Perda | Jeniang | JENG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.8 | 0 | n/a | n/a
Stage 6: 48.7Hz | Ipoh | Lumut | LMUT | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.7 | 0 | n/a | n/a
| Ipoh | Lumut Maritime | LMTM | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a
| Kuala Lumpur | Mutiara Damansara | MDAM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.7 | 0 | n/a | n/a
| Kuala Lumpur | Batu Caves | BCVS | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a
| Kluang | Parit Raja | PRJA | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a
| Kluang | Yong Peng North | YGPN | 132 | CAAH & BSPT/BKPG | 105 & 205 | 48.7 | 0 | n/a | n/a
| Seremban | Paroi | PROI | 132 | KPLH 1 & 2 | 705 & 805 | 48.7 | 0 | n/a | n/a
| Seremban | Kuala Pilah | KLPH | 132 | PROI 1 & 2 | 705 & 805 | 48.7 | 0 | n/a | n/a
| Ayer Keroh | Lipat Kajang | LKJG | 132 | JSIN & MCOP | 505 & 605 | 48.7 | 0 | n/a | n/a
| Ayer Keroh | Air Keroh | AKRH | 132 | MCOP | 205 | 48.7 | 0 | n/a | n/a
| Ayer Keroh | Ujong Pasir | UPSR | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a
| Ayer Keroh | Ujong Pasir | UPSR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a
| Ayer Keroh | Metacorp | MCOP | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a
| Ayer Keroh | Metacorp | MCOP | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.7 | 0 | n/a | n/a
| Seremban | Nilai | NLAI | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a
| Selangor | Batu Tiga | BTGA | 33 | 132/33kV T1 & T2 & T3 | 1T0 & 2T0 & 3T0 | 48.7 | 0 | n/a | n/a
| Selangor | Bukit Badong | BBDG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.7 | 0 | n/a | n/a
| Selangor | Rasa Selangor Industry | RSID | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.7 | 0 | n/a | n/a
Stage 7: 48.6Hz | Ayer Keroh | Gerisik | GRSK | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a
| Johor Bahru | Kota Putri | KPTR | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a
| Johor Bahru | Skudai | SDAI | 22 | 132/22kV T7 & T8 | 37 & 38 | 48.6 | 0 | n/a | n/a
| Johor Bahru | Larkin GIS | LKIN | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a
| Kuantan | Kg. Awah | KAWA | 132 | SONG | 605 | 48.6 | 0 | n/a | n/a
| Kuantan | Jambu Rias | JBRS | 132 | TMID | 205 | 48.6 | 0 | n/a | n/a
| Perda | Gelugor | GLGR | 33 | 132/33kV T1 & T2 & T3 | 1T0 & 2T0 & 3T0 | 48.6 | 0 | n/a | n/a
| Perda | Bayan Mutiara | BMTR | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a
| Perda | Batu Kawan South | BTWS | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a
| Perlis | Kangar | KGAR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.6 | 0 | n/a | n/a
| Selangor | Shah Alam West | SHAW | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.6 | 0 | n/a | n/a
| Selangor | Shah Alam West | SHAW | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a
| Selangor | Teluk Panglima Garang | TPGR | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.6 | 0 | n/a | n/a
| Selangor | Shah Alam North | SHAN | 11 | 132/11kV T1, T2 & T3 | 31, 32 & 33 | 48.6 | 0 | n/a | n/a
| Selangor | Shah Alam Section 18 GIS | SHLB | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a
| Selangor | Bandar Botanic | BBTC | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a
| Perda | Bedong | BDNG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a
| Kuala Lumpur | Kuala Lumpur North | KULN | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.6 | 0 | n/a | n/a
| Dungun | Dungun | DGUN | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a
| Dungun | Chendering | CHRG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.6 | 0 | n/a | n/a
Stage 8: 48.5Hz | Kluang | Kluang (New) | KLUG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.5 | 0 | n/a | n/a
| Johor Bahru | Majidee | MAJD | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a
| Dungun | Dungun Industries | DGID | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a
| Dungun | Chukai | CKAI | 33 | 132/11kV T1 & T2 | 31 & 32 | 48.5 | 0 | n/a | n/a
| Alor Setar | Tanjong Pauh | PAUH | 11 | 132/11kV T3 & T4 | 35 & 36 | 48.5 | 0 | n/a | n/a
| Perda | Bukit Minyak | BMYK | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.5 | 0 | n/a | n/a
| Perda | Bukit Minyak | BMYK | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.5 | 0 | n/a | n/a
| Perda | Prai Industries | PRID | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a
| Perda | Prai Industries | PRID | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.5 | 0 | n/a | n/a
| Selangor | Puchong Perdana | PCHP | 33 | 132/33kV T1, T2 & T3 | 1T0, 2T0 & 3T0 | 48.5 | 0 | n/a | n/a
| Selangor | Connaught Bridge PS | CBPS | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.5 | 0 | n/a | n/a
| Selangor | Bandar Baru Shah Alam | SHAB | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a
| Kuala Lumpur | Segambut | SGBT | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.5 | 0 | n/a | n/a
| Kota Bharu | Jeli | JELI | 33 | 275/33kV T1 & T2 | 1T0 & 2T1 | 48.5 | 0 | n/a | n/a
| Kota Bharu | Tanah Merah | TMRH | 132 | Pasir Putih 1 & 2 | 305 & 405 | 48.5 | 0 | n/a | n/a
| Kota Bharu | Kandis | KDIS | 132 | Pasir Putih 1 & 2 | 505 & 605 | 48.5 | 0 | n/a | n/a
Stage 9: 48.4Hz | Ayer Keroh | Kelemak | KLMK | 132 | CHNG & ZRNA | 305 & 805 | 48.4 | 0 | n/a | n/a
| Ayer Keroh | Malim Jaya | MJYA | 132 | BVTA 1 & 2 | 705 & 805 | 48.4 | 0 | n/a | n/a
| Ayer Keroh | Malacca | MCCA | 132 | BRBI 1 & 2 | 705 & 805 | 48.4 | 0 | n/a | n/a
| Ayer Keroh | Malacca | MCCA | 132 | TGBU 1 & 2 | 905 & 1005 | 48.4 | 0 | n/a | n/a
| Dungun | Kenyir Temporary | KNYT | 132 | KBRG & CHRG/KTGU | 305 & 205 | 48.4 | 0 | n/a | n/a
| Dungun | Chendering | CHRG | 132 | KBRG/KTGU & KNYT/KTGU | 205 & 305 | 48.4 | 0 | n/a | n/a
| Kluang | Bukit Batu | BBTU | 132 | SNAI & SLNG | 205 & 505 | 48.4 | 0 | n/a | n/a
| Johor Bahru | Skudai | SDAI | 132 | SNAI & SLNG | 305 & 405 | 48.4 | 0 | n/a | n/a
| Selangor | Batang Berjuntai | BTAI | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a
| Kuala Lumpur | K.L.East | KULE | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a
| Kuala Lumpur | KL Pavilion | KLPV | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a
| Perda | Tikam Batu | TKBU | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.4 | 0 | n/a | n/a
#REF! | Johor Bahru | Tampoi | TPOI | 22 | 132/22kV T1, T2 & T3 | 1T0, 2T0 & 3T0 | 48.3 | 0 | 49.3 | 120
| Kluang | Batu Pahat East | BPHE | 132 | BPHT 1 & 2 | 305 & 405 | 48.3 | 0 | 49.3 | 120
| Kluang | Yong Peng | YGPG | 132 | BPHT & TPCH | 105 & 205 | 48.3 | 0 | 49.3 | 120
| Kluang | Yong Peng | YGPG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.3 | 0 | 49.3 | 120
| Selangor | Jalan Meru | MERU | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.3 | 0 | 49.3 | 120
| Selangor | Proton | PROT | 33 | 132/33kV T1 & T2 & T3 | 1T0 & 2T0 & 3T0 | 48.3 | 0 | 49.3 | 120
| Seremban | Kilat | KLAT | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.3 | 0 | 49.3 | 120
| Alor Setar | Perlis Power Station | PLPS | 132 | TPAU | 705 | 48.3 | 0 | 49.3 | 120
| Alor Setar | Kuala Perlis | KPLS | 132 | TEWA 1 & 2 | 305 & 405 | 48.3 | 0 | 49.3 | 120
| Kuala Lumpur | Imbi | IMBI | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 5T0 | 48.3 | 0 | 49.3 | 120
| Kuala Lumpur | Kota Damansara | KDSA | 33 | 132/33kV T3 & T4 & T5 | 3T0 & 4T0 & 5T0 | 48.3 | 0 | 49.3 | 120
| Kuala Lumpur | Galloway | GWAY | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.3 | 0 | 49.3 | 120
| Perda | Bukit Tambun | BTBN | 132 | VDOR/JNKO & NBTL Feeders | 105 & 205 | 48.3 | 0 | 49.3 | 120
| Perda | Bagan Serai | BSRI | 132 | PBTR & NBTL | 105 & 205 | 48.3 | 0 | 49.3 | 120
#REF! | Perda | Sungai Pinang | SPNG | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.2 | 0 | 49.3 | 90
| Seremban | Nilai | NLAI | 132 | MTIN & AMID | 505 & 605 | 48.2 | 0 | 49.3 | 90
| Seremban | Paroi | PROI | 132 | MTIN 1 & 2 | 305 & 405 | 48.2 | 0 | 49.3 | 90
| Seremban | Mantin | MTIN | 132 | PROI 1 & 2 | 305 & 405 | 48.2 | 0 | 49.3 | 90
| Kuala Lumpur | Kajang | KJNG | 132 | KEST 1 & 2 | 105 & 205 | 48.2 | 0 | 49.3 | 90
| Kuala Lumpur | National University | NUNI | 132 | BHGT 1 & 2 | 305 & 405 | 48.2 | 0 | 49.3 | 90
| Kuala Lumpur | Bukit Mahkamah | BMKM | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.2 | 0 | 49.3 | 90
| Johor Bahru | Tebrau | TBRU | 132 | PLGI 1 & 2 | 905 & 1005 | 48.2 | 0 | 49.3 | 90
| Johor Bahru | Pasak | PSAK | 132 | PUBB & KTGI | 505 & 605 | 48.2 | 0 | 49.3 | 90
| Kluang | Renggam | RNGM | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.2 | 0 | 49.3 | 90
| Kluang | Kluang | KLUG | 132 | KLID & NYOR | 105 & 205 | 48.2 | 0 | 49.3 | 90
#REF! | Alor Setar | Kangar | KGAR | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.1 | 0 | 49.3 | 60
| Ipoh | Sri Iskandar | SIKD | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 & 1W0 | 48.1 | 0 | 49.3 | 60
| Selangor | Ladang Kundang | LKDG | 33 | 132/33kV T3 & T4 | 3T0 & 4T0 | 48.1 | 0 | 49.3 | 60
| Selangor | Subang Jaya Town Centre | SJTC | 33 | 132/33kV T1 & T2 | 1T0&2T0 | 48.1 | 0 | 49.3 | 60
| Perda | Bayan Baru | BBRU | 33 | 132/33kV T1 & T2 | 1T0 & 2T0 | 48.1 | 0 | 49.3 | 60
| Seremban | Semarak | SMRK | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.1 | 0 | 49.3 | 60
| Seremban | Semarak | SMRK | 132 | Hualon 1, 2 & 3 | 505605705 | 48.1 | 0 | 49.3 | 60
| Johor Bahru | Seelong | SELG | 11 | 132/11kV T1 & T2 | 31 & 32 | 48.1 | 0 | 49.3 | 60
| Johor Bahru | Stulang Darat | STUL | 22 | 132/22kV T1 & T2 | 1T0 & 2T0 | 48.1 | 0 | 49.3 | 60
| Kluang | Batu Pahat East | BPHE | 132 | SGAD 1 & 2 | 105 & 205 | 48.1 | 0 | 49.3 | 60
| Ayer Keroh | Sungai Abong | SABG | 132 | PJML & PYSF | 305 & 405 | 48.1 | 0 | 49.3 | 60